Introduction

This technical description and operating instruction covers the block "ALTO 2000 central control board" (hereinafter referred to as block) of Fire Alarm Control Unit with control devices of automatic fire protection "АLТО 2000" devices (hereinafter referred to as device) and are meant for studying its structure, set-up, maintenance, transportation and storage.

The external view of the block is represented in Figure 1.

The following abbreviation are used in this document:

stub line - is a two-wired electric power line to which the fire detectors, as well as end-of-line resistor and a diode could be connected.

FACIE - fire alarm control and indicating equipment;

Sensor - the same as detector;

AFFS - automatic firefighting system;

LCD - liquid crystal display;

CCF - LCD depiction of the closed-circuit fault ;

LB - LCD depiction of line break;

CCF - LCD depiction of control circuit failure;

TSR - LCD depiction of thermal sensor response;

PCS - LCD depiction of power consumption sensor;

SEA  - spare equipment and accessories;

ADC - alarm detection circuit;

SCB - startup control block;

CU - control unit;

SB - sounder beacon;

ISCAU - the in-rush starting current amplifier unit

IPS - internal power supply

TREV - terminals to which the "Fire" relay contacts are connected

NEIS - terminals to which the "Failure" relay contacts are connected

VENT - terminals to which the "Ventilation" relay contacts are connected

PS  - the power supply.

1. Intended use

The block is designed for operation in the device performance 3 and 4 according to TS 31.6-16307479-001: 2006. The block operating modes in all performances are as following:

- rest mode;

- fire alarm mode;

- fault warning mode;

- disconnect mode (Applicable only during regular maintenance work);

- disable programming mode (Applicable only when performing maintenance work);

- log view mode;

- light and sound indication test mode;

- date setting mode;

- start mode.

The unit in the device of execution 3 works as a FACIE with the possibility of expanding the functions of the fire control device when the SCB block and other devices are connected by shielded two-wire information line.

The unit in the device of execution 4 works as a FACIE and ensures:

- receiving reports of fire and malfunction detectors included in the thirty-two loops;

- ensures the issuance of a command by shielded two-wire information line for manual and automatic start of fire fighting, with the help of the unit SCB;

- ensures the issuance of a command by shielded two-wire information line for the termination, restoration and discharging of the start, with the help of the unit SCB;

- reception on the controlled duplex information line of information signals from the blocks "ALTO 2000 BCP";

- formation of alarms, malfunctions, disabling of ventilation;

- the inclusion of warning blocks ("FIRE!");

- light and sound indication of operating modes.

The scope of application consists in protection of industrial objects premises, banks, warehouses, underground and aboveground garages, tunnels, residential and administrative buildings, as well as other objects, on which, the conditions of blocks usage are constructive.

Functional features of the block:

- reception of messages from detectors connected directly to the loops of signaling (number of alarm loops is up to 32);

- the issuance of a fire alarm signal to the operator by light and sound signals indicating the number of the loop and filling in the alarm in the event log, issuing a fire alarm signal by closing the relay contact;

- issuing of a signal error to the light and sound signals operator indicating the number of the loop and filling in the failures in the event log, the issuance of a fault signal by closing the relay contact;

- the formation of the ventilation disabling signal in the automatic mode while the operation of two loops of the alarm, or when the manual start is activated;

- the light-control signal alert

- formation of a command for launching the SCB units, if the "AFFS" mode is allowed, the “Automatic mode” mode is automatically operated in two separate plugs of the block corresponding to one direction of fire extinguishing;

- formation of a command for manual start of SCB blocks in the manual and automatic fire extinguishing modes - by the operator command from the control panel of the block (by pressing the button of the corresponding zone under the cover, which bends);

- provides the issuance of an information command for the SCB blocks for the stop and restart startup by the operator from the control panel of the block by pressing the button "ON/OFF" on the shielded two-wire information line;

- provides an indication of the cease-start (LED "Delay Start");

- provides the issuance of an information team for the SCB blocks to the start disable of the SCB by the operator from the control panel of the block by pressing the "RESET" button on the shielded two-wire information line;

- the display of transmission, reception, confirmation of start-up from the corresponding SCB on the indicators of the control panel of the block;

- filling in the nonvolatile log of messages about all events and operator actions;

- automatic switch to standby power supply with indication of the power supply mode on the control panel;

- manual testing of indication bodies in the "CHECK" mode.

2. The technical specification

2.1.1. Power supply of the unit is carried out from the AC mains voltage (207 - 253) V and frequency (50 ± 1) Hz. Standby power supply - 2 batteries with a voltage of 12 V and a capacity of 7 Ah a year. Operation of the unit without batteries is forbidden.

2.1.2. The network current power supply (207 - 253) and the frequency (50 ± 1) Hz is calm - no more than 0.025 A (in the absence of voltage of the battery 220 - less than 0.08 A).

2.1.3. The block maintains functionality at single failures of the 220 V mains voltage and lasts up to 150 ms while the batteries are disconnected.

The specifications of applicable fuses:

- F1 - 0,5 A (fuse type 50 T - 0500 N);

- F2 - 2 А (fuse type 50Т – 020Н );

- F3 - 2 А (fuse type 50Т – 020Н );

- F4 - 1 А (fuse type 50Т – 010Н );

Indicators of the power supply unit (UE):

2.2.1. Voltage source (24 ± 4) V with pulsation voltage not exceeding 4 V, with maximum long-term load current (Imax.a1): 0.8 A and minimum load current (Imin1): 0 A.

2.2.2. The voltage source (-10 ± 0.5) V with a pulse voltage of not more than 1 V with

Maximum long-term load current (Imax.a2): 0.03 A and minimum load current (Imin2): 0 A.

2.3.1. Charger with a voltage source of 27.6 B (20 ºC) and a battery charge current of 300 mA.

2.3.2. With the variable ambient temperature battery voltage varies by 32 mV at 1 ° C (from 26.8 C (40 ° C) to 28.24 C (-5 ° C)).

2.3.3. The maximum internal resistance of the battery and its connecting circuits (Ri): 0,1Om

2.3.4.  Provides battery disconnection of load reduction to the output voltage up to (22 ± ± 1) V

2.3.5. The operating time of the device using fully charged batteries with a capacity of 7 Ahh is at least 24 hours in rest mode and depends on the number and types of detectors connected to the device.

2.4. The block provides an opportunity to include in a single loop of current-consuming detectors at a DC voltage in the loop (18-27) V and passive detectors, with a snap-in contact. The number of simultaneously connected detectors - up to 32 per loop, but no more than 512 detectors per block.

2.5. The block provides the possibility of issuing a control unit for supplying four-wire fire detectors (a voltage of 12 V for these detectors should be formed by an external power supply unit), while ensuring the reset of the detectors by removing the supply voltage for at least 6 seconds. Output contacts of the "12Vd" relay provide a current switching of no more than 0.8 A at a voltage up to 30 V.

2.6. Maximum resistance of alarm loops and lines without remote element must not be more than 220 ohms.

Resistance between wires cables leak alarm lines and each wire on the ground must be at least 50 ohms.

It is recommended to use cables with twisted pairs (wave resistance - 120 Ohm) for loops of signaling and communication lines.

2.7. The block has an output for connecting the light and sound alarm ("ALTO 2000 SB" block ). The load capacity of the output must not be more than 400 mA. If you need to connect a large number of SB units, make it through the contacts of the external electromagnetic relay and powered from a separate power supply unit, as shown in Annex 5.

2.8. Output contacts of "FIRE", "NEIS", "VENT" relays provide switching of the current of no more than 0,8 A at a voltage up to 30 V.

2.9. The unit saves and stores the information about the number of recorded "Alarm" (0000-9999), "Error" (0000-9999) messages in nonvolatile memory, and event log with decoding of event types. This information is displayed on the LCD in the "Log" mode.

2.10. The unit can display the current time in rest mode. The accuracy of the readings of the current time is provided in the presence of backup power supply. It is necessary to re-set the time and date after the exhaustion is complete. If the time and date have not been set, the block does not display them and does not log in.

2.11. Information capacity of the block is up to 32 units.

2.12. It could be up to 16 block units connected to the SCB by the shielded two-wire information line.

2.13. Time of technical readiness of the block for work is 30 seconds.

2.14. The unit must be operated under the following climatic conditions:

- the ambient temperature should be from -5 ° C to 40 ° C;

- the relative humidity of the air should be 93% at a temperature not more than 40 ° С;

- the atmospheric pressure should be from 84 mmHg to 107 mmHg.

2.15. Indicators of unit reliability:

- the average time for failure is at least 18,000 hours;

- the average recovery time is no more than 4 hours.

2.16. Overall dimensions of the block: 320 x 390 x 92 mm, excluding the protruding parts.

2.17. The unit weight without accumulators should not be more than 6 kg.

2.18. The operating temperature of all semiconductor components of PEG should not exceed 120ºC.

2.19.  The operating temperature of other components of PEG should not exceed 80ºC.

2.20. The date of manufacture of the device is contained in its serial number - ***MMYY***, where MM is a month, YY is year *** and is other information.

3. Scope of supply

3.1. Scope of supply contains:

- block in the case,

- Manufacturer's Data Report,

- Quality Warranty Card,

- a set of operational documentation (TM and UM) (the delivery of one set per group of devices),

- SEA set,

- package set.

The manufacturer does not supply batteries together with the product and is not responsible for the incorrect operation of the product as a result of the installation of low-quality batteries.

4. Precautions specification

4.1. It is necessary to familiarize yourself with this document before starting the work with the unit.

4.2. Ii is necessary to take the following measures that ensure the safety of the service personnel when working with the unit:

- the unit must be connected to AC mains voltage (207 - 253) V through differential relay and reliably grounded;

- the maintenance staff should be familiar with the instruction "Rules of technical operation of electrical installations and safety rules for the operation of electrical installations," which defines the requirements for the grounding of measuring equipment and precautions to be taken when working with the alternating voltage of the network.

5. The general principle of operation of the device

5.1. The block is a device that is functionally disposed in a metal case with doors opening and closing with the help of a lock with an individual key. The control panel of the block contains the indicating and control sensors necessary for the operation of the personnel with the block, which are accessible from the first (one button click) and the second (by pressing more than one button) access level. Switching elements and controls, intended for mounting and installing the block configuration and loops, are located under the lid of the door and are accessible only from the third (lock) level of access to open. Hand-operated fire extinguishing buttons are located on the control panel under the lid in sixteen directions, with the marking "Manual start buttons are under the cap! Unbend and press!".

The block is designed on the basis of a single-chip controller and functions in accordance with the microprocessor, written in the IPTV. The data on the number of accumulated messages and the current state of the block are recorded in the EEPROM chip.

5.2. The functional block diagram is shown in Figure 2.

Composition of a block:

- microcontroller;

- vendor master record,

- the loop switcher;

- power supply;

- control and indication sensors;

- electromagnetic relays;

- RS-485 communication module.

5.3. The work of the block is controlled by a microcontroller program stored in the parallel earthing conductor. Loops are continuously monitored and inquired by the microcontroller via switches. Separately fixed ccf loop, loop breakage, current change in loop. Adjustment of forks is carried out at manufacturing of a block. The block generates a message "FIRE" in the case of a current loop change and "NEIS" in case of breakdown and ccf loop, or in the case of a block diagram output (loop of the switch). The signals "FIRE" and "NEIS" are output through relay contacts.

The RS-485 module is designed to communicate with other units in a shielded two-wired information line.

5.4. The "WATCH DOG" scheme monitors the operation of the unit and, in case of failure, produces a pulse dump of the microcontroller, which allows to withdraw the unit from the state of failure.

5.5. The power supply generates secondary voltages for the circuit elements, as well as recharging the batteries. Power supply is provided by two batteries with a nominal voltage of 12 V 7 A/hours.

5.6. Control, indication and switching sensors:

- LED with red color "FIRE" glow is active during "FIRE" and "START" fire extinguishing. The glow algorithm is flashing. It is inactive when turning off and turning on the power again.

- The LED with a yellow color of the "NEIS" glow is active during the "NEIS" regime. The glow algorithm is flashing. It is inactive when turning off and turning on the power again.

- LED with yellow color "OFF" glow is active during "OFF" mode (shutdown mode). The glow algorithm is permanently enabled with at least one shutdown in the system. It is inactive when turning off and turning on the power again.

- LED with yellow glow "CHECK" - active during the "CHECK" mode (check of indicators). The glow algorithm is flashing. It is inactive when turning off and turning on the power again.

- LED with yellow glow "FIRE RELEASE" is active in the case of a malfunction or disconnection in the "FIRE RELEASE" control circuit. The glow algorithm is flashing when there is a fault in the control circuit of the relay and constantly glow when disconnected from the control circuit. It is inactive when turning off and turning on the power again.

- LED with yellow glow "NEIS" is active in the case of a malfunction or disconnection in the "NEIS" control circuit. The glow algorithm is flashing when there is a fault in the control circuit of the relay and constantly glow when disconnected from the control circuit. It is inactive when turning off and turning on the power again.

- LED with yellow glow "VENT" is active in the case of a malfunction or disconnection in the "VENT" control circuit. The glow algorithm is flashing when there is a fault in the control circuit of the relay and constantly glow when disconnected from the control circuit. It is inactive when turning off and turning on the power again.

- LED with yellow glow "SB relay" is active in the case of a malfunction or disconnection in the " SB relay" control circuit. The glow algorithm is flashing when there is a fault in the control circuit of the relay and constantly glow when disconnected from the control circuit. It is inactive when turning off and turning on the power again.

- LED with green color of the "electricity supply" glow is active in the presence of supply voltage of the block. The glow algorithm glows continuously with any supply voltage on the block.

- LED light with a yellow color "electricity supply" glow is active in the case of a malfunction in any power supply of the unit or charger. The glow algorithm is flashing.

- LED with yellow glow "SYSTEM ERROR" is active in the case of errors when accessing the system memory of the block or violation of its configuration. The glow algorithm is flashing.

The block diagram abbreviations

- WATCH DOG - Automatic reset circuit;

- RES - generated reset signal (RESET);

- MH IZM. - the measuring cables scheme parameters;

- IPS  - internal power supply.

LEDs with red color "DIRECTION OF FIREFIGHTING" in sixteen directions are active during the FIRE FIGHTING mode of the respective direction. The glow algorithm:

Blinking in meand mode for 1 sec., If start-up occurs;

- Permanent glow when the start delay is on;

- Glide 50 ms with a period of 4 seconds, if the corresponding direction is allowed and the unit is in rest mode.

It is inactive when turning off and turning on the power again.

- LED with a green glow color "AFFS" is active in the permitted mode of automatic fire extinguishing. Glow algorithm is the constant shining.

- LED with red glow "START" is active during "FIRE FIGHTING" mode. The glow algorithm is flashing. It is inactive when turning off and turning on the power again.

- LED with red color "DELAY START" is active during "FIREFIGTING" blocking mode. The glow algorithm is flashing. It is inactive when turning off and turning on the power again.

- The LED with the green color of the glow "EXCHANGE" is active only during the time of information exchange between the block.

- The two-character symbolic LCD indicator is intended for visual indication of operating modes of the device.

- “(” button – "Increment” - a service key, is used depending on the mode.

- ”(” button – "Decrease” - a service key, is used depending on the mode.

- “ADD” button. Logs in to the second level of access (confirmation of the status of the second level of access is a periodic short beep after the release of the button). It also serves to reset modes:

  - Programming blackouts - the second level of access;

  - Log view - the second level of access;

  - Installation of date - the second level of access;

to block and unblock the alert in the FIRE mode - the second level of access.

- “LOG” button. Performs:

  - Log in - the first level access,

  - The verification mode - the second level of access (clause 7.2.1),

  - The installation of date mode - the second level of access (by re-pressing),

  - Log in the programming mode of trips, and resetting the system error - the second level of access,

- "SOUND OFF" button. Blocks the sound of the built-in speaker - the first level of access.

- "DISCHARGE MODES" button resets modes of:

  - fire alarm - the second level of access;

  - the malfunction warning - the second level of access;

  - fire extinguishing - the second level of access.

- "BLOCK / UNBLOCK START" button. Blocks and (by pressing) unblocks the launch - the first level of access. Applies to active start mode.

- "LAUNCH RESET" button resets the startup mode - the first level of access. Applies to active start mode.

- The manual start buttons (1-16) activate the start mode for the SCB in this direction of fire extinguishing - the third level of access, or are used to program the mode of disconnections - the second level of access, unless a bending overlay is installed (see Figure 1) and the device does not perform fire extinguishing functions, but performs functions exclusively AFFS.

- Jumpers BL4 - BL1 indicate the number of SCBs connected to the CU. Third level of access (see Appendix 7).

- Jumpers VID, COM, ASPT Indicate the configuration of the SCB in the device. Third level of access (see appendix 7). Перемичка (джампер) SSM. Резерв

- Jumpers VP3 - VP1 indicate the operating mode of the CU zones in the device. Third level of access (see appendix 7).

- Jumper RZ. Resistor

- Jumpers G4 - G1 indicate the number of groups of loops in the device. Third level of access (see appendix 7).

- Clamping contactors for connection loops and external equipment.

All obligatory sensors of control and their work algorithms display are conformed to ISO EN 54-2.

The location of sensors of controls and indications on the block control panel is shown in Figure 4.

5.7. The 32 universal loops are connected to the block, each of them allows including detectors with normally closed contacts, normally opening contacts, current-consuming detectors, detectors used to indicate the operation of the reverse polarity pulse (IPS). The scheme of connecting detectors to the loop is shown in Figure 3.

5.8. The unit sends direct and reverse polarity pulses to the loop to power and control current-consuming detectors and control the integrity of the loop lines.

5.9. The block saves and stores the number of received "TREV" and "NEIS" messages in the non-volatile counter (EEPROM). The number of accumulated anxieties and malfunctions is displayed on the LCD in the "LOG" mode. You can view the log on the indicator using the "LOG" “(” і ”(” Buttons.

5.10. The message "FIRE" is formed by switching the contacts of the "fire" relay and the light and sound indication. In the log view mode, the LCD detects the type of detector that was triggered (CST-pin, DIP current-consuming).

5.11. The message "NEIS" is formed by switching contacts of the "neis" relay and the light and sound indication. In LCD view mode, the type of fault in the loop is deciphered (short circuit or breakage, fault of the control circuit, NO SIGNAL - violation of interlocking exchange in the complex mode of operation).

5.12. The sound reset of the built-in speaker occurs when you press the "SOUND BLOCK" button, and when you press the "DISCHARGE MODE" button (the second level of access), all modes are reset and the unit goes into rest mode.

5.13. The unit can be connected to other devices for collaboration with the help of RS-485 communication module.

5.14. The "AFFS" jumper provides the automatic fire extinguishing mode.

5.15. "KOM" Jumper activates the mode of block operation, in which the shielded two-wired information line up to 16 fire extinguishing directions are controlled.

5.16. The rest mode description.

The device takes the rest mode after switching on power or resetting modes in the absence of factors which are favorable for switching the block to other modes.

Indicator status in rest mode:

- the illuminated LED with green light "electricity supply";

- the "AFFS" and "EXCHANGE" LEDs are in a state corresponding to the chosen operating mode of the block;

- other LEDs are excluded;

- sound alarm is disabled;

- after the installation (p.7.3) a colon, or the date and time are displayed in the top line of LCD;

- relay contacts "Fire", "Neis", "Vent" and "SB" are in the passive state.

5.17. the fire alarm mode specifications.

The device switches to the fire alarm mode automatically when any fire detector is activated in any fire alarm loop.

The indicators status in fire alarm mode:

- LED illuminated with green "electricity supply" light;

- "AFFS" and "EXCHANGE" LEDs are in a state, corresponding to the chosen operating mode of the block;

- active (flashing) LED with red "FIRE" light;

- other LEDs are in a state, corresponding to another active mode;

- the sound signaling of the fire mode is activated, if there is no sound signal of the start mode;

- The LCD displays the numbers and the quantity of loops that are in operation;

The number of zones, which are given in the example, which are in the state of fire is three: the Z3, Z6 zones on the CU and one of the zones on the BCP05.

- "Fire" and "SB" relay contacts are in active state;

- contacts of the "NEIS" and "VENT" relay are in a state, which is corresponding to other active modes.

Exiting this mode is carried out from the second level of access by pressing the "MODES DISPLAY " button (the transition to the second level of access is carried out by pressing the "ADD", the confirmation of the status of the second level of access is a periodic short beep after the button is unlocked).

5.18. The fault warning mode specifications.

The device switches to the fault warning mode automatically when any fault occurs.

The indicators status in fault warning mode:

- active LED with green "electricity supply" light;

- "AFFS" and "EXCHANGE" LEDs are in a state, corresponding to the chosen operating mode of the block;

- the active (flashing) LED glows with the yellow "NEIS";

- active (flashing) yellow-colored LEDs correspon to a particular fault;

- other LEDs are in a state, corresponding to another active mode;

- acoustic alarms are activated when there is no acoustic signaling of the trigger mode or fire alarm mode;

- The LCD displays the numbers of faulty loops or other fault messages if there is no indication associated with the alarm mode display; suppressed information on faulty zones can be viewed on LCD by pressing and holding the “(” і “Add” buttons;

In the example given, the number of zones in a malfunction state is three: Z3, Z6 zones on the CU and one of the zones on the SCB05.

- contacts of the "NEIS" relay in the active state;

- the contacts of the "Fire", "Vent" and "SB" relays are in a state, corresponding to other active modes.

Exit from this mode is carried out from the second level of access by pressing the "REDUCTION MODES" button (the transition to the second level of access is carried out by pressing the "ADD" button, the confirmation of the status of the second level of access is a periodic short beep after the the button release).

5.19. Disconnect mode (Applicable only during regular maintenance work);

The unit switches to the disconnect mode (if there are any) automatically after disabling programming mode.

Indicator status in disconnecct mode:

- the active LED glows with the green "electricity supply" light;

- "AFFS" and "EXCHANGE" LEDs are in a state, corresponding to the chosen mode of operation of the block;

- active LED with yellow color "OFF";

- active LEDs glows yellow, corresponding to the specific disconnections, full information about the excluded zones can be viewed in the disabling programming mode (p. 5.20);

- other LEDs are in a state, corresponding to another active mode;

- the sound alarm is in a state, corresponding to another active mode;

- The LCD displays information about the disabled zones or information that corresponds to other active modes; suppressed information about the disabled zones can be viewed on the LCD by pressing and holding the “(” and "ADD" buttons or in the disable programming mode;

In the example given, the number of zones in the state of disconnections is three: Z3, Z6 and Z18 on the CU.

- the contacts of the "FIRE", "NEIS", "VENT" and "SB" relay are in a state, corresponding to other active modes.

The block turnes off the disconnect mode (if there are not any) automatically after turning off the disable programming mode.

5.20. Disable programming mode specifications (Applicable only when performing maintenance work).

The device switches to the disable programming mode by manual operation from the second level of access by pressing the "LOG" button (switch to the second level of access is carried out by pressing the "ADD" button, the confirmation of the status of the second level of access is a periodic short beep after the button release).

Indicators status in the disable programming mode:

- the active LED glows with the green "electricity supply" light;

- “AFFS" and "EXCHANGE" LEDs are in a state, corresponding to the chosen mode of operation of the block;

- active LED with yellow color "OFF";

- The "fire extinguishing direction" 9 - 16 LEDs display the content of the selected register; the content changes are carried out using the manual start buttons (9 to 16); the compliance table of the content of the registers to the zones that are disconnected is given in Annex 9;

- The "fire extinguishing direction" 1 - 8 LEDs display the current address of the disabled register (Annex 9), if you change the contents of the register of the selected address, then the entry of this address information is to move to the next address, the change of address is carried out by the “(” and ”(” zoom buttons;

- other LEDs are in a state, corresponding to another active mode;

- the sound alarm is in a state, corresponding to another active mode;

- LCD displays the "disable programming";

- the contacts of the "FIRE", "NEIS", "VENT" and "SB" relay are in a state, corresponding to other active modes;

Turn off the disable programming mode by pressing the "ADD" button.

5.21. Look for the log viewer mode specifications look for Chapter 7.

5.22. Look for the check mode specifications in Chapter 7.

5.23. Look for the date setting mode specifications in Chapter 7.

5.24. Look for the manual start mode specifications in Chapter 7.

5.25. Look for the automatic start mode specifications in Chapter 7.

6. Getting started

6.1. The area in which the device is installed for operation must be equipped with artificial lighting, and the block must be protected from direct influence of atmospheric precipitation. It must not be any impurities of aggressive substances in the air.

6.2. The block is attached to the wall in accordance with the marking given in Annex 1, the height of the attachment must not be less than 1.5 m from the floor.

6.3. Disconnect all supplying voltages before connecting the supply cables, check the cables externally for them not to be too bent, and their insulation is not damaged.

6.4. Ensure that the loops of the fire alarm and other external circuits are mounted in accordance with the project design of the facility fire alarm and fire extinguishing means.

6.5. Measure the full resistance of each loop and the isolation resistance of each conductor of the loop against the protective ground. Measured values should be no worse than those required in clause 2.6.

6.6. Plug the loops and equipment according to the project.

6.7. Check all the connections after the wires are connected. If errors were detected, correct them before feeding power to the appliance. After thoroughly examining all the connections, carefully spread the wires inside the enclosure along the perimeter so that they do not touch the elements of the board. According to the marking (L-Phase, N-neutral, PE-protective grounding), connect the wires of the protective grounding, then wires of power supply by 0,75 mm intersection to the block of clamps installed on the board.

6.8. If you are sure that all connections are correct, proceed to check the device for operation.

7. The block operation check

7.1. Make sure that all the end-elements of the cords (resistor R2 2.2 kOhm and VD2 diode are included in series, as shown in Figure 3) are installed in all unused loops of the clamping logs used to connect.

Using Appendix 7 to verify that the block configuration jumpers are installed correctly (changing the configuration of the unit causes a system error, to close the system error go to the programming mode of disconnections, p. 5.20, and exit the programming mode by disconnecting the button "ADD").

Connect the batteries to the block, strictly maintaining the polarity of the connection. The block will remain disabled.

Turn on the power supply of the block, in this case, the block makes a short beep and turns on the green "electricity supply" LED. The colon will appear at the top of the LCD.

Press and release the "ADD" button, after the short beeps, press and release the "DISCHARGE" button. Make sure that the "electricity supply" LED glows, the red and yellow lights are off, no sound alarms are displayed. Check the loops and equipment connections to the block, eliminate failures and return to clause 7.1.

7.2.1. The of the block indication operation check.

Press and release the "LOG" button. After a short beep the inscription appears on the LCD: "LOG: BUFFERING. FIRE____ NEIS____ ", press the "ADD" button, after the short beeps, press and release the "LOG" button again. The indicators, including all signs on the LCD, appear for a while, then disappear, and all lights will flash again, then the indicators disappear, a short beep will be issued by the SB block and the unit will enter the date setting mode. Press and release the "ADD" button, after the short beeps, press and release the "DISCHARGE MODE" button. The block will turn on the rest mode (c. 5.16).

7.2.2. The block and loops operation check.

Inform the object staff that you are going to check the block and loop operation.

Make sure the block is in rest mode. Check the loops indicators, causing them to operate, and lines of loops, causing short circuits and breaks. The unit displays alarms and errors in messages on the LCD by the corresponding blinking of indicators and a sound signal. Reset the beep by pressing the "SOUND OFF" button. The "FIRE", "NEIS" and "SB" relays work out. Alarm and fault counters increase their readings. Press and release the "ADD" button, after the short beeps, press and release the "DISCHARGE MODE" button. The block will turn on the rest mode.

Make sure that the device is switched back to the backup by disconnecting it from the main supply. In this case, the yellow "ELECTRICITY SUPPLY" LED must blink in the 60 seconds and the alarm sound of the fault warning will be activated. Reconnect the power supply, the block turns on the rest mode (the only fault, which is reset automatically). Perform reset mode after each check.

7.3. Set the current date and time when the block is checked. Press and release the "LOG" button. After a short beep the inscription will appear on the LCD: "LOG: BUFFERING. FIRE____ NEIS____ ", press the "ADD" button, after the short beeps press and release the "LOG" button again. The indicators, including all signs on the LCD, appear for a while, then disappear, and all lights will flash again, then the indicators disappear, a short beep will be issued by the SB block and the unit will enter the date setting mode. Press and release the "ADD" button, after the short beeps, press and release the "DISCHARGE MODE" button. The block will turn on the rest mode. The old time and date will appear at the top line of the LCD, the date and time are displayed in the format:

ХХ.       ХХ.    ХХХХ   ХХ   :   ХХ     (e.g., 26.03.2008 12:30)

Day   month    year    hours   minutes

There is a tip SET THE YEAR in the bottom line.

7.3.1. When you press and release the “(” and ”(” buttons, the readings increase or decrease by 1. Make the necessary statement and press the "LOG" button. The bottom line will show the following tip - SET THE MONTH.

Set the month in the same way as in steps 7.3.1, then usin tips:

SET THE DATE – set the day and the month;

SET THE YEAR – current hours;

SET THE MINUTES – current minutes and, after making sure that the given readings are correct (for accurate installation it is necessary to take into account that the counter of seconds is reset at each press of the “(” and ”(” buttons), press and release the "ADD" button, after the short beeps press and release the "DISCHARGE MODES" button. The block will turn on the rest mode. (The device will turn on the rest mode no later than in 60 seconds automatically in the absence of operator actions).

On the LCD the top line will display The current date and time will appear in the top line on the LCD. Split colon between hours and minutes will be blinking.

The time and date adjustment should be carried out in case of violation of testimony through the:

- the battery and network simultaneous disconnectiong

- day-light saving time;

- 1 March of the intercalary year;

- the reading time difference is more than 3 minutes for any reason.

If the date and time are not set after the connection of the power supply, the device would not display their readings, only the split colon would be flashing in the upper line of the LCD. Log events are recorded and reproduced without specifying the date and time.

7.4. The event log view.

Press and release the "LOG" button. After a short beep, the LCD will display:

LOG:  BUFFERING. FIRE____ NEIS____ ,

where ____ are the numerical values (from 0000 to 9999) accrued by alert and failure messages for the entire service life.

By pressing and releasing the “(” and ”(” buttons, you can view the latest events fixed by the device, while the top line of the LCD displays the time and date of the message in the following format:  ХХ.       ХХ.    ХХХХ   ХХ   :   ХХ     (e. g., 26.03.2012 12:30)

day   month    year    hours   minutes

(or only a colon, if the operator did not customize data settings before the block is used). The LCD displays the messages in the bottom line, the full type list of which is given in Appendix 9.

When the extreme values are reached (the first and last record in the event log), the double signal sounds appear when the “(” and ”(” buttons are pressed.

To exit the log view mode - press and release the "ADD" button, after the short beeps, press and release the "DISCHARGE MODE" button. The block will turn on the rest mode. (The device will enter the rest mode no later than in 60 seconds automatically in the absence of operator actions).

7.5. The device check with in the performance device 4.

7.5.1. Make sure the installation is done according to the project, the units are connected to the shielded two-wired information line as shown in Appendix 6, and the position of the jumper corresponds to the operating mode according to Appendix 7.

7.5.2. Disconnect all the initiators of the fire extinguishers mixers from the SCB overhead lines.

7.5.3. Conduct a comprehensive check of all connected SCB units, in accordance with clause 7.2 (instructions for SCB operation).

7.5.4. Check the launches by triging them by pressing the manual start buttons or by creating conditions for automatic start-up. The block displays the launches by messages on the LCD, corresponding to the flashing of indicators and an acoustic signal. Reset the light and sound signal, and also block the start, reset the start by pressing the "ADD", "SOUND OFF", "RESET START" and "REDUCTION MODE" buttons. The "FIRE", "NEIS", "VENT" and "SB" relays are working out.

8. Maintenance and operation

8.1. Recommendations to the operator when working with the device.

8.1.1. When taking up the duty, make sure that the device is in the rest mode - there are no sound and light notifications, the "ELECTRICITY SUPPLY" LED is on. Compare the meter readings of the device's alert fire and error messages with the previous ones. Identify the reasons that caused the increase in this indication (if the readings have increased) and whether they were documented by your predecessor (for example, in a special journal or in another form, as provided by the job description).

If the device, for no apparent reason, does not functioning in the way it is indicated in this manual, a fire or malfunction periodically appears or could not be reset - contact the personnel who serves the fire alarm at your device.

8.1.2. When the "FIRE" signal is received, press the "SOUND OFF" button (the sound is turned off) and operate in accordance with the employee manual. After setting and eliminating the causes of the alarm, press and release the "ADD" button, after the short beeps, press and release the "DISCHARGE" button. The block will return to rest mode. If, after eliminating the causes of the alarm and transferring the unit to rest, the alarm reappears - press the "SOUND OFF" button and contact the electromechanics that serves the device.

8.1.3. When the "NEIS" signal is received, press and release the "ADD" button, after the short beeps, press and release the "MODES DISCHARGE" button. The block will return to rest mode. If the signal appears again - press the "SOUND OFF" button and contact the electromechanics that serves the instrument.

8.1.4. In case of suspicion of improper operation of the appliance or loops, contact an electrician or technical staff serving the fire alarm system.

8.2. Maintenance is carried out in order to ensure reliable operation of the unit and is carried out by specially trained personnel.

8.3. In the period of operation the daily and weekly control, as well as scheduled work, is envisaged.

8.4. The daily control of the device includes an external inspection in accordance with clause 8.1.1.

8.5. The weekly control of the device includes an external review in accordance with clause 8.1.1 and manual testing of the operation of the block indication (clause 7.2.1).

8.6. Regular works are carried out once in 6 months and contain: external and internal review of the device in order to check the state of the case (the condition of the coating, the presence of deformations of the case, the reliability of its attachment) and the quality of fastening of the leadwires to the blocks of clamps; inspection of the block in accordance with 7.2 and 8.5 clauses.

8.7. It is necessary to check the functioning of the whole system of fire alarm once in 6 months (fire detectors, reception and control devices, devices receiving signals "Trev", "Neis"). To do this, you must perform operations in accordance with clause 7.2 of this document.

8.8. Once a year, it is necessary to check the electrical resistance between the cables of the signaling loops and the electrical resistance of the cables of the signal loop of the instrument type Ts4340 TS 25-04.3300-77, as well as if necessary (strong pollution, oxidation) to restore a reliable connection.

8.9. The defective block is repaired only in the conditions of the manufacturer!

8.10. Data about maintenance and restoration of operation must be filled in the warranty card of the product.

9. Guarantees

9.1. The seller confirms that his product meets the purpose and specifications, has no defects in the material and performance.

Terms of warranty service are described in the warranty card included in the delivery of the appliance.

9.2. The seller's obligations are fulfilled upon presentation by the user of the unit with a warranty coupon bearing the seller's mark on the sale and a passport stating the date of commissioning of the instrument.

9.3. The seller's obligations are limited to the repair of the device or to its complete replacement, if it is proved that, during operation in accordance with the technical description and the operating manual, it does not conform to the seller's specifications or it is proved that there is a defect in the material or a defect in execution.

9.4. The warranty is invalid if the device is not properly rebuilt or repaired except for the seller or manufacturer's service. All other guarantees, expressed or implied, as well as requirements for performance of any functional characteristics not specified in the documentation for the block, are not taken into account.

9.5. Under no circumstances will the seller be liable to anyone for any breach that arose as a result of a breach of the warranty.

9.6. For warranty and post-warranty service, please contact STU "ALTOSAN", LLC, 3, Pivnichna str., Kyiv city, t / f (044) 412-00-29.

Application list

Application 1.  Mounting dimensions of the device without the cover and the front panel and the order of installation of the block.

Application 2. Allocation and marking of incoming and outgoing contacts.

Application 3. Examples of detectors and loops connection (p 1 – p 3).

Application 4. The launch of the "ALTO 2000 CU" block including the "ALTO 2000" device, execution 3 and 4

Application 5. Connection of SB blocks.

Application 6. Connection of blocks by the two-wire information line.

Application 7. Jumpers configuration setting unit.

Application 8. The messages saved in the memory (log) and displayed on the LCD.

Application 9. Conformity list of the switch-off registers to zones that are disabled.

Application 1.                                   Mounting dimensions of the device without the cover and the front panel and the order of installation of the block.

- Make markings on the wall

- Prepare mounting holes that are packed

- Prepare the slots for inserting wires into the unit

- Screw the top two mounting screws with a gap of 2-3 mm

- Hang a block, insert the wires into the slots

- Screw in and bolt up the lower fixing screw of the mount

- Bolt up the two upper screws of the mount

Application 3 (sheet 1).

Examples of detectors and loops connection

A loop that consists of detectors with normally closed contacts and normally open contacts

1 – detectors with normally closed contacts

2 – detectors with normally open contacts.

Number of detectors is up to 32 pcs.

VD1-VDn is a 1N4148 semiconductor diode or any silicon diode with a reverse current of not more than 10 μA and a return voltage of at least 50 V.

A loop that consists of current consuming detectors.

1 – detectors are up to 32 pcs.

Applicatio 3 (sheet 2).

Examples of detectors and loops connection

A loop that consists of detectors of different types.

1 – detectors with normally closed contacts.

2 – current-consuming detectors.

3 – manual detectors, current-consuming with quotations.

Number of detectors is up to 32 pcs.

The Launch of the detectors, designed to work in unipolar loops.

D1:1…D2:1 – detectors are up to 32 pcs.

Application 3 (sheet 3).

Examples of the detectors and loops connection

A loop that consists of four-wire detectors.

1 – The number of four-wire detectors (type DIP 12 V and similar) is up to 16 pcs.

Uk 1 = 12 V in OKO-Relay

Application 4 (sheet 1).

The launch of the "ALTO 2000 CU" block including the "ALTO 2000" device, execution 3

Application 4 (sheet 2).

The launch of the "ALTO 2000 CU" block including the "ALTO 2000" device, execution 4

Application 5.

Connection of SB blocks

Connection of one SB block

If the SB of "ALTO 2000" SB Block type, so the VD2 diode does not need to be connected.

Connection of the additional SB block (more than 1)

Additional SBs are connected to the block output through the intermediate relay and using a separate power supply.

Application 7 (sheet 1).

Jumpers configuration setting unit

Located under the cap of the block at the top of the display board.

Purpose:

BL4...BL1 number of fire extinguishing directions assigned to the block

0000 - 1 direction	1000 -  9  directions

0001 –2 directions	1001 - 10 directions

0010 - 3 directions	1010 - 11 directions

0011 - 4 directions	1011 - 12 directions

0100 - 5 directions	1100 - 13 directions

0101 - 6 directions	1101 - 14 directions

0110 - 7 directions	1110 - 15 directions

0111 - 8 directions	1111 - 16 directions

Where: 0 - jumper not installed,

1 - jumper is installed.

VID - jumper is removed - all four start-up lines of the connected blocks of the CU, operate in one direction;

jumper is installed - all four start-up lines of the connected blocks of the CU, operate as separate directions.

KOM - jumper is removed - standby mode;

jumper is installed - mode of connection of "ALTO 2000 CU" blocks by the two-wired information line.

ASPT – jumper is installed - automatic fire extinguishing mode is allowed

VP3...VP1 - block operation mode.

000 - The block loops operate in FACIE mode and do not affect the automatic start-ups (connected CU blocks work with their loops).

100 - automatic launch is allowed in the presence of anxiety simultaneously in a pair of loops of fire alarm of the corresponding direction:

direction 1 - loops  1 and 2,

direction2 - loops 3 and 4,

:

direction16 - loops 31 and 32.

101 - automatic start is allowed in the presence of anxiety at the same time in any pair of fire lines of the corresponding direction:

direction1 – loops 1 and 2 or 3 and 4,

direction2 - loops 5 and 6 or 7 and 8,

:

ddirection8 - loops 29 and 30 or 31and32.

110 - automatic start is allowed in the presence of anxiety at the same time in any pair of fire lines of the corresponding direction:

direction1 - loops 1 and 2 or 3 and 4 or 5 and 6 or 7 and 8,

direction2 – loops 9 and 10 or 11 and 12 or 13 and 14 or 15 and 16,

:

direction4 - loops 25 and 26 or 27 and 28 or 29 and 30 or 31 and 32.

111 - automatic start is allowed in the presence of anxiety at the same time in any pair of fire lines of the corresponding direction:

direction1 – loops 1 and 2 or 3 and 4 or 5 and 6 or 7 and 8 or 9 and 10 or 11 and 12 or 13 and 14 or 15 and 16,

direction2 - loops 17 and 18 or 19 and 20 or 21 and 22 or 23 and 24 or 25 and 26 or 27 and 28 or 29 and 30 or 31 and 32.

RZ – resistor .

G4...G1 - positional code of the loops groups blocking.

0001 - loop 1 - loop 8 is blocked

0010 - loop 9 - loop 16	-/-

0100 - loop 17 - loop 24	-/-

1000 - loop 25 - loop 32	-/-

Де :	0 - jumper is removed,

1 - jumper is installed.

Application 7 (sheet 2)

# Description of the group of jumper located on the motherboard

(see application 2)

# J1 – is responsible for indicating and controlling the output +12Vd.

Must be installed unless an external 12 V source is used.

Jumper is removed - output control + 12Vd (error will be displayed as power failure).

Jumper is installed - control of output + 12Vd is disconnected.

# J2, J3, J4 – are responsible for the type of used contact relay (normally closed or normally open) of the TREV, NEIS and VENT relay respectively.

Numbering of contacts J2, J3, J4 is carried out from the bottom up in figure 5.

# Figure 5. The scheme of the output contacts of the "TREV", "NEIS", "VENT" relay.

J2, J3, J4 – jumper; VD – diod 1N4148; R – resistor ОМЛТ-0,25 -2,2 кОм±5%.

The jumper is installed on the contacts 1-2 (J2, J4) and 2-3 (J3) - the normally duplex contact of the relay is used.

The jumper is mounted on contacts 2-3 (J2, J4) and 1-2 (J3) - the normally closed contact of the corresponding relay is used.

Application 8 (sheet 1).

The messages saved in the memory (log) and displayed on the LCD

| Alert type UKR | Comment |
| --- | --- |
| СКИДАННЯ______ЦП | CU reduction |
| ПЕРЕВІРКА_____ЦП | CU check |
| СКИД.__ПУСКУ__ЦП | CU start discharge |
| БЛОК___ПУСКУ__ЦП | CU start block |
| РОЗБЛОК_ПУСК__ЦП | CU start unblock |
| НЕСП.___220В__ЦП | No 220V voltage in the CU |
| НОРМА___220В__ЦП | 220V voltage in the CU |
| НЕСП._24Восз__ЦП | No power supply of the SB in CU |
| НОРМА_24Восз__ЦП | Power supply of the SB in CU |
| НЕСП.__12Вс___ЦП | No power supply in the CU sensors |
| НОРМА__12Вс___ЦП | Power supply in the CU sensors |
| НЕСП.___АКК___ЦП | Defective CU battery |
| НОРМА___АКК___ЦП | CU working battery |
| НЕСП.__Р.ОСЗ__ЦП | The error of the SB relay circle of the CU |
| НЕСП._Р.ВЕНТ__ЦП | The error of the VENT relay circle of the CU |
| НЕСП._Р.НЕСП__ЦП | The error of the NEIS relay circle of the CU |
| НЕСП._Р.ПОЖ.__ЦП | The error of the FIRE relay circle of the CU |
| НЕСП._Заряд.__ЦП | Error of the CU charger |
| НЕСП._ Zхх____ОБР | XX CU loop breakage |
| НЕСП._ Zхх___К.З. | CCF in a XX CU loop |
| НЕСП._ Zхх____УПР | Error of the XX CU loop operation |
| ПОЖ.___Zхх___ДИП | Working out of a current-consuming detector in a XX CU loop |
| ПОЖ.___Zхх___КНТ | Operation of a contact detector in a XX CU loop |
| Р._ПУСКц_НАПР_хх | Manual start from CU of XX direction |
| А._ПУСКц_НАПР_хх | Automatic start from CU of the XX direction |
| СИС._ПОМИЛКА__ЦП | CU system error |
| НЕСП.__ОБМІН_Бхх | Вisruptions of the XX block |
| НОРМА_ОБМІНУ_Бхх | Reconnection with the block XX |
| СКИДАННЯ_____Бхх | Reset the XX block |
| ПЕРЕВІРКА____Бхх | Check the XX block |
| СКИД._ПУСКУ__Бхх | The start reset of the XX block |
| БЛОК_ПУСКУ___Бхх | Stop the start of the XX block |
| РОЗБЛ._ПУСКУ_Бхх | Restoration of the start of block XX |
| РУЧНИЙ_РЕЖИМ_Бхх | Manual mode of the XX block |
| АВТОМ._РЕЖИМ_Бхх | Automatic XX block mode |
| НЕСП.___220В_Бхх | There is no voltage 220 V in the XX block |
| НОРМА___220В_Бхх | Voltage 220 V in the XX block |
| НЕСП._24Восз_Бхх | There is no supply voltage of SB in block XX |
| НОРМА_24Восз_Бхх | There is a supply voltage of SB in block XX |
| НЕСП.___24Вп_Бхх | There is no voltage of 24 V in the starting block XX |
| НОРМА___24Вп_Бхх | There is voltage of 24 V in the starting block XX |
| НЕСП._Вx.24В_Бхх | There is no input voltage of 24V in block XX |

Application 8 (sheet 2).

The messages saved in the memory (log) and displayed on the LCD

| НОРМА_Вx.24В_Бхх | There is voltage of 24 V in the starting block XX |
| --- | --- |
| НЕСП.__12Вд__Бхх | No power supply in the CU sensors |
| НОРМА__12Вд__Бхх | There is power supply in the CU sensors |
| НЕСП.__АКК___Бxx | Defective CU battery |
| НОРМА__АКК___Бxx | CU working battery |
| НЕСП.__Р.ОСЗ_Бxx | The error of the SB relay circle of the XX |
| НЕСП._Р.ВЕНТ_Бxx | The error of the VENT relay circle of the XX |
| НЕСП._Р.НЕСП_Бxx | The error of the NEIS relay circle of the XX |
| НЕСП._Р.ПОЖ._Бxx | The error of the FIRE relay circle of the XX |
| НЕСП._Заряд._Бхх | Error of the XX charger |
| НЕСП._К.ПУСК1Бxx | The error in the circle of the manual start button 1 of the XX block |
| НЕСП._К.ПУСК2Бxx | The error in the circle of the manual start button 2 of the XX block |
| НЕСП._К.ПУСК3Бxx | The error in the circle of the manual start button 3 of the XX block |
| НЕСП._К.ПУСК4Бxx | The error in the circle of the manual start button 4 of the XX block |
| НЕСП._Л.ПУСК1Бxx | The error of line 1 of block XX |
| НЕСП._Л.ПУСК2Бxx | The error of line 2 of block XX |
| НЕСП._Л.ПУСК3Бxx | The error of line 3 of block XX |
| НЕСП._Л.ПУСК4Бxx | The error of line 4 of block XX |
| НЕСП.__КВГС1_Бxx | The error of line 1 of HCV (high calorific value) control of block XX |
| НЕСП.__КВГС2_Бxx | The error of line 2 of HCV (high calorific value) control of block XX |
| НЕСП.__КВГС3_Бxx | The error of line 3 of HCV (high calorific value) control of block XX |
| НЕСП.__КВГС4_Бxx | The error of line 4 of HCV (high calorific value) control of block XX |
| НЕСП._Р/Авт._Бxx | The error of line of the manual/automatic operation mode of block XX |
| НЕСП._Бхх_Zх_ОБР | Open circuit in the block XX of the loop X |
| НЕСП._Бхх_Zх_К.З | CCF in block XX of the loop X |
| НЕСП._Бхх_Zх_УПР | The error of the control of the block XX of loop X |
| ПОЖ.__ Бхх_Zх_ДИП | Working out of a current-consuming detector in a XX of the loop X |
| ПОЖ.__ Бхх_Zх_КНТ | Operation of a contact detector in a XX of the loop X |
| Р._ПУСК__НАПР_хх | Manual start from of XX direction |
| А._ПУСК__НАПР_хх | Automatic start from of the XX direction |
| СИС._ПОМИЛКА_Бxx | XX system error |

Application 9.

| Disconnection register 0 |
| --- |
| Addr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Loop | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

| Disconnection register 1 |
| --- |
| Addr | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Loop | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |

| Disconnection register 2 |
| --- |
| Addr | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |
| Loop | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |

| Disconnection register 3 |
| --- |
| Addr | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |
| Loop | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 |

| Disconnection register 4 |
| --- |
| Addr | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |
| Relay | FIRE control | NEIS control | VENT control | SB control | FIRE operation | NEIS operation | VENT operation | SB operation |

| Disconnection register 5 |
| --- |
| Addr | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |
| Direction | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

| Disconnection register 6 |
| --- |
| Addr | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 |
| Direction | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |

If in slots:

loop 1 - loop 32,

fire control – SB operation

zero is displayed (the corresponding LED is off), this component is turned off

If in slots:

1-16 direction the 1 is displayed (the corresponding LED is on), then this component is disabled.

Loop 1 - 32			           loops

FIRE control              			control of the "FIRE" relay contact line

NEIS control  			control of the "NEIS" relay contact line

VENT control				control of the "VENT" relay contact line

SB control				control of the "SB" relay contact line.

FIRE operation			“FIRE” relay operation

NEIS operation			“NEIS” relay operation

VENT operation			“VENT” relay operation

SB operation				“SB” relay operation

# Text boxes

Fire Alarm Control Unit

with control devices of automatic fire protection

"АLТО 2000"

ТS of Ukr. 31.6-16307479-001:2006

“Central control board

ALTO 2000” block

The technical specification

and user manual

# AADM.426429.001 TO

The 3rd addition

erection, acceleration control,

operation, service

Before you start SAT designing, erection, operation or unit maintenance examine this document carefully.

Be meticulous about this manual while erection, acceleration control and operation. This would secure the failure deficiency and provide the long-term operational stability.

“NVP ALTOSAN” LLC

3, Pivnichna str., Kyiv city

t/f (044) 412-00-29

t. (044) 411-08-33

2014

Figure 1.

The external view of the Central control board ALTO 2000” block

1 – control panel

2 – lock case

3 – markening place

4 - battening plate

1

2

3

390

4

L

N

320

Unbend and press!

Manual start buttons are unfer the cap!

Attention! In the case of a system error, only manual triggers are possible!

Receiving-control device

+line

-line

R1

2

4

3

D1

2

### Dn

4

3

### VD1

VD2

R2

loop

1	  2		  2		     3

- 1 - Detector with normally closed contacts (IPS, IP 104, PI 105, IP212-5 (relay output), etc.)

- 2 - IP 212-2 (DIP-2, DIP-3) detector and the analogical ones

- 3 - detector with normally open contacts

- R1- OMLT-0.25 - 5.1 kΩ ± 5% resistor

- R2- OMLT -0,25 - 2.2 кОм±5% resistor

- VD1, VD2 - 1N4148 semiconductor diode or any silicon diode with a reverse current of no more than 10 μA and a return voltage of at least 50 V.

Figure 3. The scheme of the detectors connection to the loop of the block.

ПОЖ. Z3

<03>

ПОЖ. Б05

Z6

Figure 4. The controls and indicators location on the control panel of the block.





Block/unblock the launch

Launch reduction

Start Delay

LCD

FIREFIGHTING DIRECTION

AFFS

START

EXCHANGE

8

1

2

3

4

5

6

7

16

9

10

11

12

13

41

15

ADD

LOG

SOUND  BLOCK

MODES DISCHARGE

NEIS

FIRE

SB relay

CHECK

OFF

Vent relay

NEIS relay

FIRE

relay

SYSTEM ERROR

electricity supply

## 1

## 2

## 10

## 9

## 3

## 4

## 12

## 11

## 5

## 6

## 14

## 13

## 7

## 8

## 16

## 15

START MANUAL FIRE FIGHTING

PRESS! Hold until beep!

NEIS. Z3

<03>

NEIS. Б05

Z6

OFF. Z3

<03>

OFF. Z18

Z6

ALTO 2000 CU block

LA  GND  LB

1

ALTO 2000 SCB block

LA  GND  LB

ALTO 2000 CU block

2

LA  GND  LB

ALTO 2000 CU block

n

(up to 16)

LA  GND  LB

Application 6.

Connection of blocks by two-wire information line

You must use screened spin pairs (FTP5) to perform the connections.

BL4 … BL1     VID         KOM         ASPT      SSM       VP3…VP1     RZ       G4   ...   G1