JSC “NPG Granit-Salamandra”

Generator of extinguishing aerosol AGS-2/4

PASSPORT

INFORMATION ON THE PRODUCT:

Generator AGS-2/4				batch No_______________

Aerosol forming compound			batch No _______________

Date of manufacturing				_______________________

The starter					Type __________ batch No ___________

MAIN TECHNICAL CHARACTERISTICS:

Semi-hermetic protected volume	up to 21 m3

Mass of aerosol forming compound	1.6 kg

Warranty period – 18 months, including 12 months of storage.

Operating life – 5 years, including 1 year of the storage

Lifetime – 10 years

After expiration of the operating period the question of its prolongation can be solved by the Manufacturer.

COMPLETENESS OF THE PACKAGE:

Generator AGS-2/4

Instruction Manual

Bracket

Generator conforms to Technical Conditions 4854-021-54876390-2003

The packing conforms to the requirements of engineering documentation

Department of technical control

Address:

JSC :NPG Granit-Salamandra”

Izhorskaya str., 13/19 125412 Moscow

Tel: 485-8454, 485-9827

JSC “NPG Granit-Salamandra”

INSTRUCTION MANUAL

For the extinguishing aerosol generators

of operational use

AGS-2/4

VEPK.634239.24 RE

Moscow, 2013

- APPLICATION

Generator of extinguishing aerosol AGS-2/4 (hereinafter – generator) is the mean of volume fire extinguishing is designed for producing of fire extinguishing aerosol and its delivery into the protected rooms for localization and suppression of fires of solid combustible materials (wood, insulating materials, plastics etc.), inflammable liquids (petrol, oil refinery products, organic solvents, etc.), electrical insulating materials and electrical live equipment with voltage up to 40 kV. Generators can be used for fire suppression in the rooms with cables, alive electrical equipment, for fire extinguishing in the railroad, motor transport, sea and river crafts.

Generators are not applied for extinguishing of alkaline metals, as well as for extinguishing of substances which are burning without air access.

Generators AGS-7 are manufactured in following modifications: AGS-2/4-1-1, AGS-2/4-1-2, AGS-2/4-1-3, AGS-2/4-1-4, AGS-2/4-2-1, AGS-2/4-2-2, AGS-2/4-2-3 and AGS-2/4-2-4

- TECHNICAL CHARACTERISTICS OF GENERATOR AGS-2/4

Mass of generator:

AGS-2/4				4.6 kg +/- 0.3 kg

Mass of aerosol forming compound:		1.6 +/- 0.1 kg

Aerosol extinguishing ability			0.05 kg/m3

Maximum volume of protected semi-hermetic room (δ  < 0.001 m-1*):  21 m3

*) δ – is ratio of the total area of the openings to the volume of protected room

Dimensions (without bracket):

- Diameter				167 +/- 2 mm

- Height					175 +/- 3 mm

Operating period:				45 +/- 5 sec

Fire extinguishing ability of aerosol for fire suppression of Class A2 and B fires and for localization of fires of class A1 is 0.075 kg/m3.

Operating conditions:

- Temperature				from – 50 °C to + 50 °C

- Relative humidity			up to 98% at 25 °C

- Mechanical effect 			group M25 GOST 17516.1-90

By way of activation generators AGS-2/4 are divided for generators with electrical, heat and combined start-up. Generators AGS-2/4 are supplied with the starter.

Fire extinguishing aerosol is produced by AGS-2/4 and delivered directly into the protected room.

Usage of electrical starters allows to use generators as a part of automatic aerosol fire extinguishing systems.

Characteristics of electrical signal necessary for the start up of generator and for control of electric starting chain during operation of generator as part of aerosol fire extinguishing system:

Electrical starter VEL (is installed inside):

- Voltage – 12 – 24 V

- Minimum starting current – 0.4A

- Type of current – direct (DC)

- Duration of impulse – not less than 0.5 sec

- Resistance of electrical initiator of the starter – 2.5 – 4.5 Om (without additional resisters)

Maximum current of control of generator starting chain should not exceed:

- At constant control – 0.005 A

- At periodical control during no more than 2 minutes with breaks not less than 10 minutes – 0.05A.

Electrical starter VR-7,5 (is installed inside):

- Voltage – 12 – 24 V

- Minimum starting current – 1.0A

- Type of current – direct (DC)

- Duration of impulse – not less than 1.5 sec

- Resistance of electrical initiator of the starter –7.5 – 8.0 Om (without additional resisters)

Maximum current of control of generator starting chain should not exceed:

- At constant control – 0.005 A

- At periodical control during no more than 2 minutes with breaks not less than 10 minutes – 0.05A.

Electrical starter UZT-7,5 (is installed inside):

- Voltage – 12 – 24 V

- Minimum starting current – 1.0A

- Type of current – direct (DC)

- Duration of impulse – not less than 1.5 sec

- Resistance of electrical initiator of the starter –7.5 – 8.0 Om (without additional resisters)

Maximum current of control of generator starting chain should not exceed:

- At constant control – 0.005 A

- At periodical control during no more than 2 minutes with breaks not less than 10 minutes – 0.05A.

Electrical starter UZ-7,5 (is installed inside):

- Voltage – 12 – 24 V

- Minimum starting current – 1.0A

- Type of current – direct (DC)

- Duration of impulse – not less than 1.5 sec

- Resistance of electrical initiator of the starter –7.5 – 8.0 Om (without additional resisters)

Maximum current of control of generator starting chain should not exceed:

- At constant control – 0.005 A

- At periodical control during no more than 2 minutes with breaks not less than 10 minutes – 0.05A.

The starter type should be chosen by the Buyer.

Thermochemical and combined starters activate the generator when the temperature in the protected volume reaches 160 – 170 ⁰C.

Heat quantity which is distinguished during generator operation, no more:

AGS-2/4		4809 kJ

Composition of products of burning:

| Component | Concentration, mg/m3 | Volume fraction, % | Concentration, mg/g relatively |
| --- | --- | --- | --- |
| NH3 | 46 | 0.0066 | 0.287 |
| NO2 | 27.6 | 0.0015 | 0.172 |
| HCN | 24.3 | 0.0022 | 0.152 |
| CO | 570 | 0.05 | 3.563 |
| CH4 | 262 | 0.04 | 1.637 |

Mass composition of the dispersed phase:

2K2CO3*3H2O		52.7%

KH4HCO3		25.7%

KHCO3			8.2%

KNO3			7.9%

Other			5.5%

Generator keeps its integrity and efficiency and does not spontaneously start after the free fall from the height of 1 m on the concrete layer with the thickness not less than 100 mm or on the steel sheet with the thickness not less than 16 mm.

The time lag (operating time) in the whole operating temperature range is no more than 2 sec.

According to GOST 19433-88 generators are not the hazardous cargo and should not be specially marked.

Electrical resistance between generator body and terminals for connecting of the starting chain at the normal climatic conditions should be not less than 1 MOm (according to GOST 15150-69).

Probability of trouble-free start-up is 0.98, probability of generator failure is no more than 0.04.

The maximum temperature of generator shell during and after its operation  should not exceed 150 °C.

The value of ozone depleting potential of aerosol does not exceed 0.01.

- DEFINING OF THE NECESSARY QUANTITY OF GENERATORS AGS-2/4 AND THEIR ALLOCATION IN THE PROTECTED ROOM

  - Generators should be installed in such way to provide quick and even filling of the protected room with the aerosol and to minimize aerosol outflow through the opened doors, windows, ventilation etc.

  - If several generators are used for protection of one space, their simultaneous activation should be provided.

  - There should be provided the forced shutdown of ventilation in the protected room after starters activation.

  - Generators should be located in the protected rooms according the flowing requirements:

    - The location of generator and the direction of nozzles should be chosen that way to provide the most free spreading of the aerosol flow which enters from the injector.

    - The distance from generator to the fence or wall, electrical equipment, cables should be not less than 10 mm;

    - Generators can not be installed on the burning basement;

    - The should be an access to installed generator for control and prevention works.

  - The choice of the installation site should be done taking in account the temperature zones and zones of fire safety.

- PREPARATION OF GENERATOR FOR OPERATION AND ITS ACTIVATION

  - Generators are anchored of the room walls with the attached brackets.

  - Generator connection to the starting chains is done after the complex of commissioning of the whole system of fire alarm is completed.

  - During connection of the starting chain wires to generator, the bridge between the terminals should be removed.

.

- ACCIDENT PREVENTION DURING INSTALLATION AND OPERATION

  - During work with generators and starters it should be considered that they contain the inflammable compositions

  - The aerosol does not contain the toxic compounds in quantities which can be dangerous for humans, but the aerosol particles can irritate the mucosa. This irritation can be neutralized by protection of the respiratory with the fabric bandage or gauze.

  - It should be kept in mind that during generator operation the temperature zone is created in which the temperature reaches the following values:

  - Size of zone with temperature over 400 ⁰C – 0.15 m

  - Size of zone with temperature over 200 ⁰C – 0.5 m

  - Size of zone with temperature over 75 ⁰C – 1.0 m

The maximum temperature of generator body during and after its operation can not exceed 150 ⁰C. Generator cup can be heated up to 500 ⁰C.

The size of fire safety zone is 500 mm.

IT IS FORBIDDEN:

- The falling of generators or their stroke;

- To use generators improperly;

- To make the welding at a distance less than 2 meters from generator;

- To use damaged generators;

- Dismantle the generator.

- MARKING, PACKING, STORAGE AND TRANSPORTATION OF GENERATORS AGS-2/4

  - There are serial numbers of aerosol forming compound, generator, manufacturing date, mass of compound and maximum protected volume in the passport and on the label of generator. The information on the label should be kept during the whole lifetime of generator.

  - Generators are supplied by the Manufacturer packed into the pasteboard boxes.

  - Generators and starters in Manufacturer’s packing can be transported by all means of transportation.

  - Generators should be stored in the Manufacturer packing in the closed storage rooms under the temperature from +5°C to +40°C and relative humidity up to 80% without the presence of aggressive environment.

  - According to GOST 19433-88 generators are not the hazardous cargo and should not be specially marked.

  - Generators can be stored in a pile, but no higher than 3 stages one on another (according to the Manufacturer packing)