OPERATING MANUAL

For the fire extinguishing aerosol generators

AGS-6/1

CONTENTS

1. INTENDED USE………………………………………………………………………………………………………………………………3

2. DESIGN……….…………………………………………………………………………………………………………………………………3

3. OPERATING PRINCIPLE………………………………………………………………………………………………………………….4

4. TECHNICAL DATA………………………………………………………………………………………………………………………….4

5.  DETERMINATION OF NECESSARY QUANTITY OF GENERATORS AGS-6/1 AND THEIR ALLOCATION IN THE PROTECTED VOLUMES………………………………………………………………………………………………………….5

6. PRE-STARTING PROCEDURE…………………………………..……………………………………………………………………..6

7. SAFETY MEASURES DURING INSTALLATION AND OPERATION OF THE GENERATORS….………………..6

8. MARKING, PACKING, TRANSPORTATION AND STORAGE OF GENERATORS……………………………………7

9. PASSPORT……………………………………………………………………………………………………………………………………..8

- APPLICATION

Generator of fire extinguishing aerosol AGS-6/1 (hereinafter – generator) is the mean of volume fire extinguishing is designed for localization and suppression of fires of solid combustible materials (wood, insulating materials, plastics etc.), inflammable liquids (petrol, oil refinery products, organic solvents, etc.), electrical insulating materials and electrical live equipment with voltage up to 40 kV.

Generators can be used for fire protection of small volumes (electrical cabinets, engine compartments, etc.), power systems of high voltage, including systems used on means of transportation, as they conform the requirements to vibration strain on railway, auto and air transport.

Generators should be used in accordance with the valid norms (SP 5.13130.2009 “Automatic fire alarm and fire extinguishing systems”)

Generators are not applied for extinguishing of alkaline metals, as well as for extinguishing of substances which are burning without air access.

- DESIGN

Generator consists of the body (1) inside which an aerosol forming compound (2) and the starter (3) are located.   Aerosol forming compound is separated from the shell of the body by the heat insulating material (4). To reduce the temperature of aerosol flow the cooler (5) is used, which is located between the compound and the side surface of the body.  There are nozzle holes (6) in the side surface of the body through which the aerosol comes out. The threaded sleeve for binding of the starter is located in the cover of generator. Generator is installed in the protected room with the special tenons (7), which are welded to generator body.

Generators AGS-6/1 can be activated with electrical, heat or combined starters. The starters can be inbuilt or can be supplied separately from the generator and installed during the assembly.

In special modification the jack (8) is anchored on generator cover for connection of electrical starter.

- PRINCIPAL OF OPERATION

After the electric or heat impulse reaches the starter, the aerosol forming compound is ignited. Aerosol is produced in the process of burning of the solid aerosol forming compound which is located inside the generator shell. Aerosol flow penetrates through the cooler and enters the protected volume.

- TECHNICAL DATA

Mass of equipped generator:			1.20 +0.12 kg

Mass of aerosol forming compound:		0.35 +/- 0.01 kg

Aerosol extinguishing ability			0.100 kg/m3

Maximum volume of protected semi-hermetic room (δ  < 0.001 m-1*): 		3.2m3

* δ – is ratio of the total area of the openings to the volume of protected room

Operating period:				19 +/- 2 sec

Dimensions (without brackets):

- Diameter				122 mm

- Height                                                            69 mm

Operating conditions:

- Temperature				from – 50 °C to + 50 °C

- Relative humidity at 25 	°C		up to 80%

- The generator AGS-6/1 conforms to mechanical version group M25 according to GOST 17516-90

- Mechanical effect of 1 g in the frequency band up to 100 Hz

For generator activation the special starters are used: electrical, thermochemical and combined.

The use of thermochemical starters which activate when the temperature in the protected volume reaches 180 ⁰C, allows each generator to operate autonomously.

The use of electrical starters allows to use generators as part of automatic aerosol fire extinguishing systems.

Characteristics of electrical signal necessary to start up the generator and to control the electric starting chain during operation of generator as part of aerosol fire extinguishing system:

Electrical starter VEL, VELTH –combined, with thermochemical cord (is installed outside):

- Minimum starting current – 0.4A

- Maximum starting current – 5A

- Type of current – direct (DC)

- Duration of impulse – not less than 0.5 sec

- Resistance of electrical initiator of the starter – 2.5 – 4.5 Om (without additional resisters)

Electrical starter VRp-7,5, VRTHp-7,5 – combined, with thermochemical cord (is installed outside):

- Minimum starting current – 1.5A

- Maximum starting current – 2A

- Type of current – direct (DC)

- Duration of impulse – not less than 3 sec

- Resistance of electrical initiator of the starter –7.5 – 8.0 Om (without additional resisters)

Maximum current of control of generator starting chain should not exceed:

- At constant control – 0.005 A

- At periodical control during no more than 2 minutes with breaks not less than 10 minutes – 0.05A.

The starter type should be chosen by the Buyer.

Heat quantity which is distinguished during generator operation:	1020 kJ

Generator keeps its integrity and efficiency and does not spontaneously start after the free fall from the height of 1 m on the concrete layer with the thickness not less than 100 mm or on the steel sheet with the thickness not less than 16 mm.

The time lag (operating time) in the whole operating temperature range is no more than 2 sec.

Permissible voltage for electric installations is determined according to breakdown voltage rate in the environment «aerosol + air». (Annotational record notification of Federal State Institution Fire Safety Research Institute of Russian Federation Ministry of Civil Defense and Emergency Response) «Research of breakdown voltage rate determination in the environment «aerosol + air».

- DETERMINATION OF THE NECESSARY QUANTITY OF GENERATORS AGS-6/1 AND THEIR ALLOCATION IN THE PROTECTED VOLUMES

  - The design and installation work on aerosol fire extinguishing systems should be fulfilled by the specialized organizations which have the license for such type of service. Calculation of generator quantity necessary for protection of the given room is made according to the methodology contained in the valid norms (SP 5.13130.2009 “Automatic fire alarm and fire extinguishing systems”, Fire Regulations 88-2001 “Fire extinguishing and alarm systems. Design norms and rules”).

  - Generators are recommended to be installed in the lower part of protected room such way to provide quick and even filling of the protected room with the aerosol and to minimize aerosol outflow through the openings (hatches, gates, ventilation etc.) .

  - Generators should be located in the protected rooms according the following requirements:

    - The distance from generator to the fence or wall,  to the equipment, wiring, electrical appliances  should be not less than 200 mm;

    - The distance between generators should be not less than 200 mm;

    - Generators can not be installed on the burning basement;

    - There should be an access to installed generator for control and prevention works.

  - If several generators are used for protection of one space, their simultaneous activation should be provided.

  - If generators with electrical starter are used, the forced switch off of ventilation before generators activation should be provided.

  - For reducing of starting period of generator with thermochemical starter, it is recommended to install in the protected room with heat sensitive cord which should be allocated in the upper part of the room and in the places of most possible ignition. The cord should be connected to the heat sensitive element of the starter.

  - If several generators are installed in one room, thermochemical starters should be connected between each other with the heat sensitive cord.  This provides simultaneous staring of generators.

- PRE-STARTING PROCEDURE

  - Generator is anchored on the room walls or fences.

  - After generator is mounted and the whole installation of the fire extinguishing system is finished, the starter  is screwed into the threaded sleeve in the central opening of generator.

  - During installation of thermochemical starter it is necessary to keep heat sensitive cord undamaged.

In special modification generators are supplied with inbuilt electrical starters which are connected to the jack. It is necessary to remove the barrier from the jack (if any) before connecting the generator to the starting chain.

- SAFETY MEASURES DURING INSTALLATION AND OPERATION OF THE GENERATORS

  - During work with generators and starters it should be considered that they contain the inflammable compositions

  - During installation of electrical starters the endings of cables should be shorted.

In case of special modification the barrier on the jack is used for shorting of electrical starter. This barrier is removed during the mounting.

Before connecting the starter to the starting chain it is necessary to make sure that there is no voltage.

  - Electrical equipment of premises in which generators with electrical starters are installed should conform to requirements of Rules of Electric systems operation.

  - At the design of generator electrical starting chains there should be provided the measures which exclude the appearance of current pickup which can lead to the accidental start of generators.

  - The aerosol does not contain the toxic compounds in quantities which can be dangerous for humans, but the aerosol particles can irritate the mucosa. This irritation can be neutralized by protection of the respiratory with the fabric bandage or gauze.

  - The false starting of generator AGS-6/1 in the carriages of Russian Railroads is impossible. Generator should be started remotely, manually by the designated person after evacuation of the passengers.

  - After generator has been activated it is necessary to remove the products of burning and the settled aerosol from the surfaces within 3 days, because aerosol is hygroscopic and has a week alkaline reaction after moisture absorption. The cleaning is done with the brusher vacuum cleaner and the wet cloth. The cleaning is done using individual protective gear (particulate respirator and rubber gloves).

  - In a standby mode generator does not gave a harmful influence on people and environment.

  - Possibility of the generator AGS-6/1 usage in rooms that conform the conditions of presence of people in carriages should be confirmed by Safety and Health Certificate issued by railway transportation Chief State Medical Officer

  - The activating electrical signal voltage should not exceed 36 V.

  - Generators used as part of automatic fire extinguishing system should be located in protected premises taking in account the fire hazards zones. Generators should not be activated before evacuation is completed.

  - Technical service is aimed to prevent failing in the operation of generator, to maintain it at permanent readiness, providing it’s fail-free operation in case of fire.

  - Technical service of generators includes visual inspection of generators presence in the installation sites, mounting security, entirety and mounting security of generator’s supply lines.

  - Generators should not be repaired and if a fault is detected or after triggering should be replaced.

IT IS FORBIDDEN:

- To use generators for manual extinguishing of fire;

- To make the welding at a distance less than 2 meters from generator;

- To use damaged generators;

- Dismantle the generator.

- MARKING, PACKING, STORAGE AND TRANSPORTATION OF GENERATORS

  - There are serial numbers of aerosol forming compound, generator, type and batch of starter, manufacturing date, mass of compound and maximum protected volume in the passport.

  - Generators are supplied by the Manufacturer packed into the pasteboard boxes.

  - According to GOST 19433 generators are not the hazardous cargo and should not be specially marked.

  - Generators should be stored in the Manufacturer packing in the closed storage rooms under the temperature from +5°C to +40°C and relative humidity up to 80% without the presence of aggressive environment.

  - Generators can be stored in a pile, but no higher than 5 stages one on another (according to the Manufacturer packing)

JSC “NPG Granit-Salamandra”

Generator of extinguishing aerosol AGS-6/1

PASSPORT

INFORMATION ON THE PRODUCT:

Generator AGS-6/1				batch No_______________

Date of manufacturing	                                          _______________________

Aerosol forming compound			batch No _______________

Starter						type_________ batch_______

Modification                                                               ________________________

MAIN TECHNICAL CHARACTERISTICS:

Mass of aerosol forming compound	0.32 kg

Protected volume	up to 3.2 m3

Warranty period – 18 months.

Operating period – 5 years.

Lifetime – 10 years.

After expiration of the operating period the question of its prolongation can be solved by the Manufacturer.

After expiration of the lifetime period the question of its utilization can be solved by the Manufacturer.

COMPLETENESS OF THE PACKAGE:

Generator AGS-6/1

Instruction Manual with passport

Generator is completed with the starter in accordance with the order.

Package

Generator conforms to Technical Conditions 4854-062-54876390-2014

The packing conforms to the requirements of engineering documentation

Department of technical control

Address of JSC “NPG Granit-Salamandra”

127411, Moscow, Dmitrovskoe shosse, 157 building 11

Tel.: 8 (495) 641 23 82, fax: 8 (495) 641 23 81.

sales@grsl.ru